## INPUTS - SUMMARY
Power Plant Configuration (INPUTS) |  |  |  |  | Financial Model Assumptions
Power Plant Key Cost Scaling Variables |  |  |  |  | Share of Debt | % | 80
PB Installed Capacity (Gross) | kW | 100000 |  |  | Share of Equity | % | 20
Solar Field Aperture Area (Mirror Area) | m2 | 1529073.507 |  |  | Debt Interest Rate | % | 5
Thermal Energy Storage Capacity | MWh-th | 1500 |  |  | Equity IRR | % | 8
Receiver Power (Max Rated) | MW-th | 728.155 | ** Set to 0 if the CSP plant is a Parabolic Trough (PT) Technology |  | Lifetime of the plant (Operating period) | years | 30
Tower Height (w/o Receiver) | m | 194.227 | ** Set to 0 if the CSP plant is a Parabolic Trough (PT) Technology |  | Construction period | years | 2
Electric Heater Thermal Power (Max Rated) | kW-th | 250000 | ** Set to 0 if there is no electric heater installed for hybridization |  | Decommissioning costs | MUSD | 0
Land Area CSP | m2 | 9783758.11 |  |  | Decommissioning period | years | 0
PV Installed Capacity | Wdc | 100001238.876 |  |  | Depreciation | - | -
Battery Pack Power (Max Rated) | MW | 0 | ** Set to 0 if there is no battery pack |  | Taxes | - | -
Battery Pack Capacity | MWh-e | 0 | ** Set to 0 if there is no battery pack
Battery Annual Generation (for OPEX) | GWh/y | 0 | ** Set to 0 if there is no battery pack
Land Area PV | m2 | 38507297.178
CSP Annual Generation (for OPEX) | GWh/y | 203.887
Distance to Grid | km | 0
Distance to Road | km | 0
Distance to Gas | km | 0 | ** Set to 0 if there is no need for Gas line
Distance to Water | km | 0 | ** Set to 0 if there is no need for water line
Other Component Size | TBD | 0 | ** Set to 0 if ther is no other component to be included, otherwise set also a reference cost in CAPEX and OPEX
DIRECT CAPEX: | 708.5354 | MUSD | 82.6446 | % |  |  |  | TOTAL OPEX: | 8.199 | MUSD
INDIRECT CAPEX: | 148.7924 | MUSD | 17.3554 | %
TOTAL CAPEX: | 857.3278 | MUSD

## CAPEX
Power Plant Inputs (Auto-Update from INPUTS-SUMMARY) |  |  |  | * Light blue fields are reference values. These are site and tech dependent.
Reference Parameters |  |  |  | * If tower technology: SET BOP Reference to 74.8 MUSD
Installed Capacity (Gross) | kW | 100000 |  | * If tower technology: SET Solar Field Reference Cost to 125 MUSD
Solar Field Aperture Area (Mirror Area) | m2 | 1529073.507 |  | * If PT technology: SET BOP Reference Cost to 90.2 MUSD
Thermal Energy Storage Capacity | MWh-th | 1500 |  | * If PT technology: SET Solar Field Reference Cost to 115 MUSD
Receiver Power (Max Rated) | MW-th | 728.155 |  | * Set right PV module and tracking costs depending on technology used
Tower Height (w/o Receiver) | m | 194.227 |  |  | P-Si = 0.28 $/Wdc
Electric Heater Thermal Power (Max Rated) | kW-th | 250000 |  |  | Mono-Si = 0.33 $/Wdc
Land Area | m2 | 9783758.11 |  |  | Thin Film = 0.3 $/Wdc
PV Installed Capacity | Wdc | 100001238.876
Battery Pack Power (Max Rated) | MW | 0
Battery Pack Capacity | MWh-e | 0
Battery Annual Generation (for OPEX) | GWh/y | 0
Land Area PV | m2 | 38507297.178
CSP Annual Generation (for OPEX) | GWh/y | 203.887
Distance to Grid | km | 0
Distance to Road | km | 0
Distance to Gas | km | 0
Distance to Water | km | 0
Other Component Size | TBD | 0
479.535
Cost Model Reference Inputs | [6 empty] | SUMMARY OF CAPEX RESULTS
Reference Parameters |  |  | Reference Cost |  | Specfic Costs (REF) |  |  | DIRECT CAPEX: | 708.5354 | MUSD | 82.6446 | %
ST Installed Capacity (Gross) | kW | 190000 | 87.5 | MUSD | 460.5263 | USD/kW |  | INDIRECT CAPEX: | 148.7924 | MUSD | 17.3554 | %
Balance of Plant (BOP) | kW | 110000 | 90.2 | MUSD | 820 | USD/kW |  | TOTAL CAPEX: | 857.3278 | MUSD
Solar Field Aperture Area | m2 | 1000000 | 118 | MUSD | 118 | USD/m2
Thermal Energy Storage Capacity | MWh-th | 3271 | 66 | MUSD | 20.1773 | USD/kwh-th
Receiver Power (Max Rated) | MW-th | 565 | 55 | MUSD | 97345.1327 | USD/MW-th
Tower Height (w/o Receiver) | m | 200 | 30 | MUSD | 150000 | USD/m
Land Area (for CSP Site Preparation) | m2 | 5000000 | 10 | MUSD | 2 | USD/m2
Electric Heater | kW | 1000000 | 70 | MUSD | 70 | USD/kW-t
Grid Connection Costs | km | 1 | 1.5 | MUSD | 1.5 | USD/km
Road Costs | km | 1 | 1.2 | MUSD | 1.2 | USD/km
Gas Pipeline Costs | km | 1 | 1 | MUSD | 1 | USD/km
Water Pipeline Costs | km | 1 | 1 | MUSD | 1 | USD/km
Battery Pack Power (Max Rated) | MW | 1 | 0.225 | MUSD | 225 | USD/kW-e
Battery Pack Capacity (replacement included) | MWh-e | 1 | 0.30305 | MUSD | 303.05 | USD/kWh-e
Other Component | - | 1 | 0 | MUSD | 0 | USD/-
PV Modules | Wdc-peak | 1000000 | 0.3 | MUSD | 0.3 | USD/Wdc-p
PV Inverters | Wdc-peak | 1000000 | 0.1 | MUSD | 0.1 | USD/Wdc-p
PV BOS | Wdc-peak | 1000000 | 0.3 | MUSD | 0.3 | USD/Wdc-p
PV SA Tracking | Wdc-peak | 1000000 | 0.2 | MUSD | 0.2 | USD/Wdc-p
Land Area (for PV Site Preparation) | m2 | 5000 | 0.01 | MUSD | 2 | USD/m2
0.9
CAPEX Cost Model
Direct CAPEX
Sub-Block (Breakdown) | COEFF | Scaling Param | Cost |  | Specific Costs
CSP Power Block | 0.8 | 100000 | 52.3607 | MUSD | 523.6067 | USD/kW
CSP BOP | 0.8 | 100000 | 83.5781 | MUSD | 835.7808 | USD/kW
CSP TES | 0.8 | 1500 | 35.373 | MUSD | 23.582 | USD/kwh-th
CSP SF | 1 | 1529073.507 | 180.4307 | MUSD | 118 | USD/m2
CSP Receiver | 0.2 | 728.155 | 57.8626 | MUSD | 79464.642 | USD/MW-th
CSP Tower | 0.8 | 194.227 | 29.3052 | MUSD | 150881.2724 | USD/m
CSP Site Preparations / Civil works | 0.9 | 9783758.11 | 18.2971 | MUSD | 1.8701 | USD/m2
Electric Heater | 1 | 250000 | 17.5 | MUSD | 70 | USD/kW
Grid Connection Costs | 1 | 0 | 0 | MUSD | #DIV/0! | USD/km
Road Costs | 1 | 2 | 2.4 | MUSD | 1.2 | USD/km
Gas Pipeline Costs | 1 | 0 | 0 | MUSD | #DIV/0! | USD/km
Water Pipeline Costs | 1 | 0 | 0 | MUSD | #DIV/0! | USD/km
Battery Pack - Power | 1 | 0 | 0 | MUSD | 0 | USD/kW
Battery Pack - Capacity | 1 | 0 | 0 | MUSD | 0 | USD/kWh-e
Other Component | 1 | 0 | 0 | MUSD | 0 | USD/-
PV Modules | 1 | 100001238.876 | 30.0004 | MUSD | 0.3 | USD/Wdc-p
PV Inverters | 1 | 100001238.876 | 10.0001 | MUSD | 0.1 | USD/Wdc-p
PV BOS (except Inverters) | 1 | 100001238.876 | 30.0004 | MUSD | 0.3 | USD/Wdc-p
PV additional rack (SA tracking) | 1 | 100001238.876 | 20.0002 | MUSD | 0.2 | USD/Wdc-p
PV Site Preperations / Civil works | 1 | 38507297.178 | 77.0146 | MUSD | 2 | USD/m2
DIRECT CAPEX Sub-Total |  |  | 644.1231 | MUSD | 3220.5954 | USD/kW
Contingencies | - | 0.1 | 64.4123 | MUSD | 644.1231 | USD/kW
DIRECT CAPEX Total |  |  | 708.5354 | MUSD | 3542.6549 | USD/kW
Indirect CAPEX
Developer Costs | - | 0.07 | 49.5975 | MUSD | 495.9748 | USD/kW
Financial Costs | - | 0 | 0 | MUSD | 0 | USD/kW
Engineering Costs | - | 0.14 | 99.195 | MUSD | 991.9495 | USD/kW
INDIRECT CAPEX Total |  |  | 148.7924 | MUSD | 743.9575 | USD/kW
INDIRECT CAPEX Total |  |  | 857.3278 | MUSD | 4286.6125 | USD/kW

## OPEX
Power Plant Inputs (Auto-Update from INPUTS-SUMMARY)
Reference Parameters |  |  |  | * Light blue fields are reference values. These are site and tech dependent.
Installed Capacity (Gross) | kW | 100000 |  | * Depending on PV tracking, set right OPEX
Solar Field Aperture Area (Mirror Area) | m2 | 1529073.507 |  |  | Fixed Trackers | 1 | % of CAPEX
Thermal Energy Storage Capacity | MWh-th | 1500 |  |  | Single Axis Tracking | 1.75 | % of CAPEX
Receiver Power (Max Rated) | MW-th | 728.155
Tower Height (w/o Receiver) | m | 194.227
Electric Heater Thermal Power (Max Rated) | MW-th | 250000
Land Area | m2 | 9783758.11
PV Installed Capacity | Wdc | 100001238.876
Battery Pack Power (Max Rated) | MW | 0
Battery Pack Capacity | MWh-e | 0
Battery Annual Generation (for OPEX) | GWh/y | 0
Land Area PV | m2 | 38507297.178
CSP Annual Generation (for OPEX) | GWh/y | 203.887
Distance to Grid | km | 0
Distance to Road | km | 0
Distance to Gas | km | 0
Distance to Water | km | 0
Other Component Size | TBD | 0
Cost Model Reference Inputs | [7 empty] | SUMMARY OF OPEX RESULTS
Labor Costs | [8 empty] | TOTAL CAPEX: | 8.199 | MUSD
Reference Parameters |  |  | Reference Cost |  | Specfic Costs (REF)
CSP Admin/Finance & Management | kW | 110000 | 196100 | USD | 1.7827 | USD/kW
CSP Plant Operations Labor | kW | 110000 | 1335600 | USD | 12.1418 | USD/kW
CSP Plant Maintenance Labor | kW | 110000 | 286200 | USD | 2.6018 | USD/kW
CSP Solar Field Maintenance Labor | m2 | 977628 | 212000 | USD | 0.21685 | USD/m2
Service Costs
Reference Parameters |  |  | Reference Cost |  | Specfic Costs (REF)
CSP Subcontracted Services | GWh/y | 516 | 227900 | USD | 441.6667 | USD/GWh/y
Battery Pack - Fixed OPEX | MW | 0.001 | 6.9 | USD | 6.9 | USD/kW
Battery Pack - Variable OPEX | GWh/y | 0.001 | 2.1 | USD | 2.1 | USD/MWh/y
Utilitiy Costs
Reference Parameters |  |  | Reference Cost |  | Specfic Costs (REF)
CSP Electricity Use | kW | 110000 | 1431000 | USD | 13.0091 | USD/kW
CSP Water Use | kW | 110000 | 1025232 | USD | 9.3203 | USD/kW
Miscellaneous
Reference Parameters |  |  | Reference Cost |  | Specfic Costs (REF)
Other OPEX | - | 1 | 0 | USD | 0 | USD/-
CSP Machinery | kW | 110000 | 216240 | USD | 1.9658 | USD/kW
CSP Spare Parts | kW | 516 | 1331360 | USD | 2580.155 | USD/kW
OPEX Cost Model
Direct OPEX
Sub-Part (Breakdown) | COEFF | Scaling Param | Cost |  | Specific Costs
CSP Admin/Finance & Management | 1 | 100000 | 178272.7273 | USD | 1.7827 | USD/kW
CSP Plant Operations Labor | 0.7 | 100000 | 1249400.0839 | USD | 12.494 | USD/kW
CSP Plant Maintenance Labor | 0.7 | 100000 | 267728.5894 | USD | 2.6773 | USD/kW
CSP Solar Field Maintenance Labor | 1 | 1529073.507 | 331581.7299 | USD | 0.21685 | USD/m2
CSP Subcontracted Services | 0.7 | 203.887 | 118976.7795 | USD | 583.5427 | USD/GWh/y
CSP Electricity Use | 1 | 100000 | 1300909.0909 | USD | 13.0091 | USD/kW
CSP Water Use | 1 | 100000 | 932029.0909 | USD | 9.3203 | USD/kW
CSP Machinery | 0.7 | 100000 | 202283.8231 | USD | 2.0228 | USD/kW
CSP Spare Parts | 0.7 | 203.887 | 695045.7443 | USD | 3408.9753 | USD/GWh/y
Battery Pack - Fixed OPEX | 1 | 0 | 0 | USD | #DIV/0! | USD/kW
Battery Pack - Variable OPEX | 1 | 0 | 0 | USD | #DIV/0! | USD/MWh/y
Other OPEX | 1 | 0 | 0 | USD | 0 | USD/-
Fixed PV OPEX | 0.0175 | 100001238.876 | 2922774.9135 | USD | 29.2274 | USD/kW
OPEX Total |  |  | 8.199 | MUSD | 40.9948 | USD/kW